## README
PCS APPLE-TO-APPLE COMPARISON — MASTER WORKBOOK
Purpose | Structured, apple-to-apple technical/commercial evaluation of BESS PCS vendors. Feeds the HTML dashboard.
How to use | 1) Fill PCS_Master_Data (one row per Parameter × Vendor). 2) Export that sheet as CSV named PCS_Master_Data.csv. 3) Open the HTML dashboard and upload the CSV.
Data entry rule | Enter Value + Unit + Test_Condition + Source for every performance figure. Never compare a value without its test condition.
Missing data | Leave Vendor_Value blank → dashboard shows "Data Pending". NEVER treat missing data as pass or fail.
Comparison_Type | Higher_Better / Lower_Better / Range / Boolean / Text. Drives PASS/FAIL logic.
Compliance logic | Higher_Better: value ≥ Requirement_Min = PASS. Lower_Better: value ≤ Requirement_Max = PASS. Range: vendor range must cover required range. Boolean: YES vs required YES.
Scoring | Each parameter scored 0–10, weighted by category (see Parameter_Master). Final score normalized to 100.
Critical override | Critical=YES parameters that FAIL trigger CRITICAL NON-COMPLIANCE; that vendor cannot rank first regardless of score.
Category weights | Performance 18, Grid 14, DC 7, AC 8, Thermal 9, Safety 9, Cert 7, Comms 5, BESS 4, Reliability 5, Basic 4, Overload 4, Mechanical 3, Commercial 3 (=100).
Sheets | README · PCS_Master_Data · Requirements · Parameter_Master · Vendor_List · Certification · Commercial · Scoring · Dashboard_Data

## PCS_Master_Data
Category | Subcategory | Parameter | Parameter_ID | Unit | Requirement | Requirement_Min | Requirement_Max | Preferred_Value | Comparison_Type | Weight | Critical | Vendor | Model | Vendor_Value | Test_Condition | Source | Source_Date | Remarks
Basic Configuration | Type | PCS Type | P001 |  | Central/String |  |  |  | Text | 2 | NO | DemoVolt PCS-A | DV-2500-L | Central |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Type | PCS Type | P001 |  | Central/String |  |  |  | Text | 2 | NO | GridCore PCS-B | GC-2500-A | Central |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Type | PCS Type | P001 |  | Central/String |  |  |  | Text | 2 | NO | PowerStack PCS-C | PS-2200-L | String |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Type | PCS Architecture | P002 |  | Modular preferred |  |  |  | Text | 2 | NO | DemoVolt PCS-A | DV-2500-L | Modular |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Type | PCS Architecture | P002 |  | Modular preferred |  |  |  | Text | 2 | NO | GridCore PCS-B | GC-2500-A | Modular |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Type | PCS Architecture | P002 |  | Modular preferred |  |  |  | Text | 2 | NO | PowerStack PCS-C | PS-2200-L | Modular |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Rated Power | P003 | kW | ≥ 2500 | 2500 |  | 2500 | Higher_Better | 5 | YES | DemoVolt PCS-A | DV-2500-L | 2500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Rated Power | P003 | kW | ≥ 2500 | 2500 |  | 2500 | Higher_Better | 5 | YES | GridCore PCS-B | GC-2500-A | 2500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Rated Power | P003 | kW | ≥ 2500 | 2500 |  | 2500 | Higher_Better | 5 | YES | PowerStack PCS-C | PS-2200-L | 2200 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Maximum Power | P004 | kW | ≥ 2500 | 2500 |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 2750 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Maximum Power | P004 | kW | ≥ 2500 | 2500 |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 2600 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Maximum Power | P004 | kW | ≥ 2500 | 2500 |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 2400 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Continuous Power | P005 | kW | ≥ 2500 | 2500 |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 2500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Continuous Power | P005 | kW | ≥ 2500 | 2500 |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 2500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Power | Continuous Power | P005 | kW | ≥ 2500 | 2500 |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 2200 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Modular/Standalone | P006 |  | Modular |  |  |  | Text | 2 | NO | DemoVolt PCS-A | DV-2500-L | Modular |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Modular/Standalone | P006 |  | Modular |  |  |  | Text | 2 | NO | GridCore PCS-B | GC-2500-A | Modular |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Modular/Standalone | P006 |  | Modular |  |  |  | Text | 2 | NO | PowerStack PCS-C | PS-2200-L | Modular |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Number of Power Modules | P007 | nos |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Basic Configuration | Config | Number of Power Modules | P007 | nos |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Basic Configuration | Config | Number of Power Modules | P007 | nos |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Basic Configuration | Config | Parallel PCS Capability | P008 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Parallel PCS Capability | P008 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Parallel PCS Capability | P008 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Transformer Requirement | P009 | [5 empty] | Text | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Basic Configuration | Config | Transformer Requirement | P009 | [5 empty] | Text | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Basic Configuration | Config | Transformer Requirement | P009 | [5 empty] | Text | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Basic Configuration | Config | Transformer Integrated | P010 | [5 empty] | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Transformer Integrated | P010 | [5 empty] | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Config | Transformer Integrated | P010 | [5 empty] | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Cooling | Cooling Type | P011 |  | Liquid/Forced air |  |  |  | Text | 3 | NO | DemoVolt PCS-A | DV-2500-L | Liquid |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Cooling | Cooling Type | P011 |  | Liquid/Forced air |  |  |  | Text | 3 | NO | GridCore PCS-B | GC-2500-A | Forced air |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Cooling | Cooling Type | P011 |  | Liquid/Forced air |  |  |  | Text | 3 | NO | PowerStack PCS-C | PS-2200-L | Liquid |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Enclosure | IP Rating | P012 | IP | ≥ 54 | 54 |  | 65 | Higher_Better | 4 | NO | DemoVolt PCS-A | DV-2500-L | 65 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Enclosure | IP Rating | P012 | IP | ≥ 54 | 54 |  | 65 | Higher_Better | 4 | NO | GridCore PCS-B | GC-2500-A | 66 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Enclosure | IP Rating | P012 | IP | ≥ 54 | 54 |  | 65 | Higher_Better | 4 | NO | PowerStack PCS-C | PS-2200-L | 54 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Install | Installation Type | P013 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Basic Configuration | Install | Installation Type | P013 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Basic Configuration | Install | Installation Type | P013 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Basic Configuration | Install | Indoor/Outdoor | P014 |  | Outdoor |  |  |  | Text | 2 | NO | DemoVolt PCS-A | DV-2500-L | Outdoor |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Install | Indoor/Outdoor | P014 |  | Outdoor |  |  |  | Text | 2 | NO | GridCore PCS-B | GC-2500-A | Outdoor |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Basic Configuration | Install | Indoor/Outdoor | P014 |  | Outdoor |  |  |  | Text | 2 | NO | PowerStack PCS-C | PS-2200-L | Outdoor |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | Minimum DC Voltage | P015 | V | ≤ 1000 |  | 1000 |  | Lower_Better | 4 | YES | DemoVolt PCS-A | DV-2500-L | 1000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | Minimum DC Voltage | P015 | V | ≤ 1000 |  | 1000 |  | Lower_Better | 4 | YES | GridCore PCS-B | GC-2500-A | 950 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | Minimum DC Voltage | P015 | V | ≤ 1000 |  | 1000 |  | Lower_Better | 4 | YES | PowerStack PCS-C | PS-2200-L | 1100 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | Nominal DC Voltage | P016 | V |  |  |  |  | Range | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
DC Electrical | Voltage | Nominal DC Voltage | P016 | V |  |  |  |  | Range | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
DC Electrical | Voltage | Nominal DC Voltage | P016 | V |  |  |  |  | Range | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
DC Electrical | Voltage | Maximum DC Voltage | P017 | V | ≥ 1500 | 1500 |  | 1500 | Higher_Better | 4 | YES | DemoVolt PCS-A | DV-2500-L | 1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | Maximum DC Voltage | P017 | V | ≥ 1500 | 1500 |  | 1500 | Higher_Better | 4 | YES | GridCore PCS-B | GC-2500-A | 1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | Maximum DC Voltage | P017 | V | ≥ 1500 | 1500 |  | 1500 | Higher_Better | 4 | YES | PowerStack PCS-C | PS-2200-L | 1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | DC Operating Voltage Range | P018 | V | 1000-1500 | 1000 | 1500 |  | Range | 5 | YES | DemoVolt PCS-A | DV-2500-L | 1000-1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | DC Operating Voltage Range | P018 | V | 1000-1500 | 1000 | 1500 |  | Range | 5 | YES | GridCore PCS-B | GC-2500-A | 950-1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Voltage | DC Operating Voltage Range | P018 | V | 1000-1500 | 1000 | 1500 |  | Range | 5 | YES | PowerStack PCS-C | PS-2200-L | 1100-1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Current | Rated DC Current | P019 | A |  |  |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
DC Electrical | Current | Rated DC Current | P019 | A |  |  |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
DC Electrical | Current | Rated DC Current | P019 | A |  |  |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
DC Electrical | Current | Maximum DC Current | P020 | A |  |  |  |  | Higher_Better | 3 | YES | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
DC Electrical | Current | Maximum DC Current | P020 | A |  |  |  |  | Higher_Better | 3 | YES | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
DC Electrical | Current | Maximum DC Current | P020 | A |  |  |  |  | Higher_Better | 3 | YES | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
DC Electrical | Current | Continuous DC Current | P021 | A |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
DC Electrical | Current | Continuous DC Current | P021 | A |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
DC Electrical | Current | Continuous DC Current | P021 | A |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
DC Electrical | Current | DC Overload Current | P022 | A |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
DC Electrical | Current | DC Overload Current | P022 | A |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
DC Electrical | Current | DC Overload Current | P022 | A |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
DC Electrical | Quality | DC Ripple Current | P023 | % | ≤ 3 |  | 3 |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
DC Electrical | Quality | DC Ripple Current | P023 | % | ≤ 3 |  | 3 |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
DC Electrical | Quality | DC Ripple Current | P023 | % | ≤ 3 |  | 3 |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
DC Electrical | Accuracy | DC Voltage Accuracy | P024 | % | ≤ 1 |  | 1 |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
DC Electrical | Accuracy | DC Voltage Accuracy | P024 | % | ≤ 1 |  | 1 |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
DC Electrical | Accuracy | DC Voltage Accuracy | P024 | % | ≤ 1 |  | 1 |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
DC Electrical | Accuracy | DC Current Accuracy | P025 | % | ≤ 1 |  | 1 |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
DC Electrical | Accuracy | DC Current Accuracy | P025 | % | ≤ 1 |  | 1 |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
DC Electrical | Accuracy | DC Current Accuracy | P025 | % | ≤ 1 |  | 1 |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
DC Electrical | Protection | DC Isolation | P026 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | DC Isolation | P026 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | DC Isolation | P026 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Insulation Monitoring | P027 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Insulation Monitoring | P027 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Insulation Monitoring | P027 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Reverse Polarity Protection | P028 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Reverse Polarity Protection | P028 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Reverse Polarity Protection | P028 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | DC Contactor | P029 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | DC Contactor | P029 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | DC Contactor | P029 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Pre-charge Function | P030 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Pre-charge Function | P030 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Pre-charge Function | P030 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | DC Fuse | P031 |  | YES |  |  |  | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | DC Fuse | P031 |  | YES |  |  |  | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | DC Fuse | P031 |  | YES |  |  |  | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Ground Fault Detection | P032 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Ground Fault Detection | P032 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
DC Electrical | Protection | Ground Fault Detection | P032 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Power | Rated AC Power | P033 | kVA | ≥ 2500 | 2500 |  |  | Higher_Better | 5 | YES | DemoVolt PCS-A | DV-2500-L | 2500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Power | Rated AC Power | P033 | kVA | ≥ 2500 | 2500 |  |  | Higher_Better | 5 | YES | GridCore PCS-B | GC-2500-A | 2500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Power | Rated AC Power | P033 | kVA | ≥ 2500 | 2500 |  |  | Higher_Better | 5 | YES | PowerStack PCS-C | PS-2200-L | 2200 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Power | Maximum AC Power | P034 | kVA |  |  |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Power | Maximum AC Power | P034 | kVA |  |  |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Power | Maximum AC Power | P034 | kVA |  |  |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
AC Electrical | Voltage | AC Voltage | P035 | V | 690 |  |  |  | Range | 4 | YES | DemoVolt PCS-A | DV-2500-L | 690 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Voltage | AC Voltage | P035 | V | 690 |  |  |  | Range | 4 | YES | GridCore PCS-B | GC-2500-A | 690 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Voltage | AC Voltage | P035 | V | 690 |  |  |  | Range | 4 | YES | PowerStack PCS-C | PS-2200-L | 690 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Voltage | AC Voltage Range | P036 | V |  |  |  |  | Range | 3 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Voltage | AC Voltage Range | P036 | V |  |  |  |  | Range | 3 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Voltage | AC Voltage Range | P036 | V |  |  |  |  | Range | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
AC Electrical | Freq | AC Frequency | P037 | Hz | 50 |  |  |  | Range | 3 | NO | DemoVolt PCS-A | DV-2500-L | 50 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Freq | AC Frequency | P037 | Hz | 50 |  |  |  | Range | 3 | NO | GridCore PCS-B | GC-2500-A | 50 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Freq | AC Frequency | P037 | Hz | 50 |  |  |  | Range | 3 | NO | PowerStack PCS-C | PS-2200-L | 50 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Freq | Frequency Range | P038 | Hz | 47.5-51.5 |  |  |  | Range | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Freq | Frequency Range | P038 | Hz | 47.5-51.5 |  |  |  | Range | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Freq | Frequency Range | P038 | Hz | 47.5-51.5 |  |  |  | Range | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
AC Electrical | Current | Rated AC Current | P039 | A |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Current | Rated AC Current | P039 | A |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Current | Rated AC Current | P039 | A |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
AC Electrical | Current | Maximum AC Current | P040 | A |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Current | Maximum AC Current | P040 | A |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Current | Maximum AC Current | P040 | A |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
AC Electrical | PF | Power Factor Range | P041 |  | -1 to +1 |  |  |  | Range | 3 | NO | DemoVolt PCS-A | DV-2500-L | -1 to +1 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | PF | Power Factor Range | P041 |  | -1 to +1 |  |  |  | Range | 3 | NO | GridCore PCS-B | GC-2500-A | -1 to +1 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | PF | Power Factor Range | P041 |  | -1 to +1 |  |  |  | Range | 3 | NO | PowerStack PCS-C | PS-2200-L | -0.9 to +0.9 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Reactive | Reactive Power | P042 | kVAr |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Reactive | Reactive Power | P042 | kVAr |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Reactive | Reactive Power | P042 | kVAr |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
AC Electrical | Reactive | Reactive Power at Rated Power | P043 | kVAr |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Reactive | Reactive Power at Rated Power | P043 | kVAr |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Reactive | Reactive Power at Rated Power | P043 | kVAr |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
AC Electrical | Quality | THDi | P044 | % | ≤ 3 |  | 3 | 2 | Lower_Better | 4 | NO | DemoVolt PCS-A | DV-2500-L | 2.1 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Quality | THDi | P044 | % | ≤ 3 |  | 3 | 2 | Lower_Better | 4 | NO | GridCore PCS-B | GC-2500-A | 2.5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Quality | THDi | P044 | % | ≤ 3 |  | 3 | 2 | Lower_Better | 4 | NO | PowerStack PCS-C | PS-2200-L | 3.2 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Quality | DC Injection | P045 | % | ≤ 0.5 |  | 0.5 |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 0.3 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Quality | DC Injection | P045 | % | ≤ 0.5 |  | 0.5 |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 0.4 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Quality | DC Injection | P045 | % | ≤ 0.5 |  | 0.5 |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 0.5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Quality | AC Voltage THD | P046 | % | ≤ 3 |  | 3 |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Quality | AC Voltage THD | P046 | % | ≤ 3 |  | 3 |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Quality | AC Voltage THD | P046 | % | ≤ 3 |  | 3 |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
AC Electrical | Config | Three Phase | P047 |  | YES |  |  |  | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Config | Three Phase | P047 |  | YES |  |  |  | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Config | Three Phase | P047 |  | YES |  |  |  | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
AC Electrical | Config | Grid Connection Type | P048 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
AC Electrical | Config | Grid Connection Type | P048 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
AC Electrical | Config | Grid Connection Type | P048 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Performance & Efficiency | Efficiency | Maximum Efficiency | P049 | % | ≥ 99 | 99 |  | 99 | Higher_Better | 5 | NO | DemoVolt PCS-A | DV-2500-L | 99 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Maximum Efficiency | P049 | % | ≥ 99 | 99 |  | 99 | Higher_Better | 5 | NO | GridCore PCS-B | GC-2500-A | 98.8 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Maximum Efficiency | P049 | % | ≥ 99 | 99 |  | 99 | Higher_Better | 5 | NO | PowerStack PCS-C | PS-2200-L | 98.5 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 10% Load | P050 | % |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L | 97.5 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 10% Load | P050 | % |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A | 97 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 10% Load | P050 | % |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L | 96.5 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 25% Load | P051 | % |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 98.5 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 25% Load | P051 | % |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 98.2 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 25% Load | P051 | % |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 97.8 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 50% Load | P052 | % | ≥ 98 | 98 |  |  | Higher_Better | 4 | NO | DemoVolt PCS-A | DV-2500-L | 99 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 50% Load | P052 | % | ≥ 98 | 98 |  |  | Higher_Better | 4 | NO | GridCore PCS-B | GC-2500-A | 98.7 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 50% Load | P052 | % | ≥ 98 | 98 |  |  | Higher_Better | 4 | NO | PowerStack PCS-C | PS-2200-L | 98.2 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 75% Load | P053 | % |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 98.9 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 75% Load | P053 | % |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 98.6 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 75% Load | P053 | % |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 98.1 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 100% Load | P054 | % | ≥ 98 | 98 |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 98.7 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 100% Load | P054 | % | ≥ 98 | 98 |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 98.4 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Efficiency @ 100% Load | P054 | % | ≥ 98 | 98 |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 97.9 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | European Efficiency | P055 | % | ≥ 98.5 | 98.5 |  |  | Higher_Better | 4 | NO | DemoVolt PCS-A | DV-2500-L | 98.7 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | European Efficiency | P055 | % | ≥ 98.5 | 98.5 |  |  | Higher_Better | 4 | NO | GridCore PCS-B | GC-2500-A | 98.5 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | European Efficiency | P055 | % | ≥ 98.5 | 98.5 |  |  | Higher_Better | 4 | NO | PowerStack PCS-C | PS-2200-L | 98 | 50% load, 1250Vdc, 25°C | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Efficiency | Weighted Efficiency | P056 | % |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  | 50% load, 1250Vdc, 25°C |  |  | Data Pending
Performance & Efficiency | Efficiency | Weighted Efficiency | P056 | % |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  | 50% load, 1250Vdc, 25°C |  |  | Data Pending
Performance & Efficiency | Efficiency | Weighted Efficiency | P056 | % |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  | 50% load, 1250Vdc, 25°C |  |  | Data Pending
Performance & Efficiency | Aux | Standby Power | P057 | W |  |  |  |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Standby Power | P057 | W |  |  |  |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Standby Power | P057 | W |  |  |  |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Standby Consumption | P058 | W |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Standby Consumption | P058 | W |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Standby Consumption | P058 | W |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Night-time Consumption | P059 | W |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Night-time Consumption | P059 | W |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Night-time Consumption | P059 | W |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Performance & Efficiency | Aux | Auxiliary Consumption | P060 | W |  |  |  |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 350 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Aux | Auxiliary Consumption | P060 | W |  |  |  |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 420 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Performance & Efficiency | Aux | Auxiliary Consumption | P060 | W |  |  |  |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 105% Overload Duration | P061 | s |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Overload Capability | Overload | 105% Overload Duration | P061 | s |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Overload Capability | Overload | 105% Overload Duration | P061 | s |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Overload Capability | Overload | 110% Overload Duration | P062 | s | ≥ 60 | 60 |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 600 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 110% Overload Duration | P062 | s | ≥ 60 | 60 |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 120 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 110% Overload Duration | P062 | s | ≥ 60 | 60 |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 60 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 120% Overload Duration | P063 | s | ≥ 60 | 60 |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 120 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 120% Overload Duration | P063 | s | ≥ 60 | 60 |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 60 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 120% Overload Duration | P063 | s | ≥ 60 | 60 |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 30 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 125% Overload Duration | P064 | s |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Overload Capability | Overload | 125% Overload Duration | P064 | s |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Overload Capability | Overload | 125% Overload Duration | P064 | s |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Overload Capability | Overload | 150% Overload Duration | P065 | s |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L | 5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 150% Overload Duration | P065 | s |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A | 2 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Overload | 150% Overload Duration | P065 | s |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Overload Capability | Current | Maximum AC Current (Overload) | P066 | A |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Overload Capability | Current | Maximum AC Current (Overload) | P066 | A |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Overload Capability | Current | Maximum AC Current (Overload) | P066 | A |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Overload Capability | Current | Maximum DC Current (Overload) | P067 | A |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Overload Capability | Current | Maximum DC Current (Overload) | P067 | A |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Overload Capability | Current | Maximum DC Current (Overload) | P067 | A |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Overload Capability | Fault | Short Circuit Current | P068 | A |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 6000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Fault | Short Circuit Current | P068 | A |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 5000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Fault | Short Circuit Current | P068 | A |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 4000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Overload Capability | Fault | Fault Current Contribution | P069 | A |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Overload Capability | Fault | Fault Current Contribution | P069 | A |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Overload Capability | Fault | Fault Current Contribution | P069 | A |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Grid Support | Mode | Grid Following | P070 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Mode | Grid Following | P070 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Mode | Grid Following | P070 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Mode | Grid Forming | P071 |  | YES |  |  |  | Boolean | 5 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Mode | Grid Forming | P071 |  | YES |  |  |  | Boolean | 5 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Mode | Grid Forming | P071 |  | YES |  |  |  | Boolean | 5 | YES | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | LVRT | P072 |  | YES |  |  |  | Boolean | 5 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | LVRT | P072 |  | YES |  |  |  | Boolean | 5 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | LVRT | P072 |  | YES |  |  |  | Boolean | 5 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | HVRT | P073 |  | YES |  |  |  | Boolean | 4 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | HVRT | P073 |  | YES |  |  |  | Boolean | 4 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | HVRT | P073 |  | YES |  |  |  | Boolean | 4 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | Frequency Ride Through | P074 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | Frequency Ride Through | P074 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | RideThrough | Frequency Ride Through | P074 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Active Power Control | P075 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Active Power Control | P075 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Active Power Control | P075 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Reactive Power Control | P076 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Reactive Power Control | P076 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Reactive Power Control | P076 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Volt-VAR | P077 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Volt-VAR | P077 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Volt-VAR | P077 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Volt-Watt | P078 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Volt-Watt | P078 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Volt-Watt | P078 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Frequency-Watt | P079 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Frequency-Watt | P079 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Frequency-Watt | P079 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Droop Control | P080 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Droop Control | P080 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Control | Droop Control | P080 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Dynamic | Active Power Ramp Rate | P081 | %/s |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Grid Support | Dynamic | Active Power Ramp Rate | P081 | %/s |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Grid Support | Dynamic | Active Power Ramp Rate | P081 | %/s |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Grid Support | Dynamic | Reactive Power Response Time | P082 | ms |  |  |  |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Grid Support | Dynamic | Reactive Power Response Time | P082 | ms |  |  |  |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Grid Support | Dynamic | Reactive Power Response Time | P082 | ms |  |  |  |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Grid Support | Dynamic | Active Power Response Time | P083 | ms | ≤ 100 |  | 100 |  | Lower_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 30 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Dynamic | Active Power Response Time | P083 | ms | ≤ 100 |  | 100 |  | Lower_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 50 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Dynamic | Active Power Response Time | P083 | ms | ≤ 100 |  | 100 |  | Lower_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 80 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Black Start | P084 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Black Start | P084 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Black Start | P084 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Islanding Operation | P085 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Islanding Operation | P085 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Islanding Operation | P085 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Synchronization Time | P086 | s |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Grid Support | Advanced | Synchronization Time | P086 | s |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Grid Support | Advanced | Synchronization Time | P086 | s |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Grid Support | Advanced | Virtual Synchronous Machine | P087 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Virtual Synchronous Machine | P087 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Virtual Synchronous Machine | P087 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Synthetic Inertia | P088 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Synthetic Inertia | P088 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Grid Support | Advanced | Synthetic Inertia | P088 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Minimum Operating Temperature | P089 | °C | ≤ -20 |  | -20 |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | -30 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Minimum Operating Temperature | P089 | °C | ≤ -20 |  | -20 |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A | -25 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Minimum Operating Temperature | P089 | °C | ≤ -20 |  | -20 |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | -20 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Maximum Operating Temperature | P090 | °C | ≥ 60 | 60 |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 60 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Maximum Operating Temperature | P090 | °C | ≥ 60 | 60 |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 60 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Maximum Operating Temperature | P090 | °C | ≥ 60 | 60 |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 55 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Full Rated Power Temperature | P091 | °C | ≥ 50 | 50 |  | 55 | Higher_Better | 5 | YES | DemoVolt PCS-A | DV-2500-L | 55 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Full Rated Power Temperature | P091 | °C | ≥ 50 | 50 |  | 55 | Higher_Better | 5 | YES | GridCore PCS-B | GC-2500-A | 50 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Full Rated Power Temperature | P091 | °C | ≥ 50 | 50 |  | 55 | Higher_Better | 5 | YES | PowerStack PCS-C | PS-2200-L | 45 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Derating Start Temperature | P092 | °C | ≥ 50 | 50 |  |  | Higher_Better | 4 | NO | DemoVolt PCS-A | DV-2500-L | 55 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Derating Start Temperature | P092 | °C | ≥ 50 | 50 |  |  | Higher_Better | 4 | NO | GridCore PCS-B | GC-2500-A | 50 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Derating Start Temperature | P092 | °C | ≥ 50 | 50 |  |  | Higher_Better | 4 | NO | PowerStack PCS-C | PS-2200-L | 45 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Temp | Maximum Temperature | P093 | °C |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Thermal & Environmental | Temp | Maximum Temperature | P093 | °C |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Thermal & Environmental | Temp | Maximum Temperature | P093 | °C |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Thermal & Environmental | Temp | Temperature Derating | P094 | %/°C |  |  |  |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Thermal & Environmental | Temp | Temperature Derating | P094 | %/°C |  |  |  |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Thermal & Environmental | Temp | Temperature Derating | P094 | %/°C |  |  |  |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Thermal & Environmental | Storage | Minimum Storage Temperature | P095 | °C |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Thermal & Environmental | Storage | Minimum Storage Temperature | P095 | °C |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Thermal & Environmental | Storage | Minimum Storage Temperature | P095 | °C |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Thermal & Environmental | Storage | Maximum Storage Temperature | P096 | °C |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Thermal & Environmental | Storage | Maximum Storage Temperature | P096 | °C |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Thermal & Environmental | Storage | Maximum Storage Temperature | P096 | °C |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Thermal & Environmental | Env | Relative Humidity | P097 | % | 0-100 |  |  |  | Range | 2 | NO | DemoVolt PCS-A | DV-2500-L | 0-100 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Relative Humidity | P097 | % | 0-100 |  |  |  | Range | 2 | NO | GridCore PCS-B | GC-2500-A | 0-100 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Relative Humidity | P097 | % | 0-100 |  |  |  | Range | 2 | NO | PowerStack PCS-C | PS-2200-L | 5-95 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Maximum Altitude | P098 | m | ≥ 3000 | 3000 |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 4000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Maximum Altitude | P098 | m | ≥ 3000 | 3000 |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 4000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Maximum Altitude | P098 | m | ≥ 3000 | 3000 |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 3000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Altitude Derating | P099 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Thermal & Environmental | Env | Altitude Derating | P099 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Thermal & Environmental | Env | Altitude Derating | P099 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Thermal & Environmental | Cooling | Cooling Type | P100 | [5 empty] | Text | 2 | NO | DemoVolt PCS-A | DV-2500-L | Liquid |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Cooling | Cooling Type | P100 | [5 empty] | Text | 2 | NO | GridCore PCS-B | GC-2500-A | Forced air |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Cooling | Cooling Type | P100 | [5 empty] | Text | 2 | NO | PowerStack PCS-C | PS-2200-L | Liquid |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Cooling | Cooling Power Consumption | P101 | W |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Thermal & Environmental | Cooling | Cooling Power Consumption | P101 | W |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Thermal & Environmental | Cooling | Cooling Power Consumption | P101 | W |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Thermal & Environmental | Env | Noise | P102 | dB | ≤ 80 |  | 80 |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 72 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Noise | P102 | dB | ≤ 80 |  | 80 |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 75 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Noise | P102 | dB | ≤ 80 |  | 80 |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 80 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Enclosure | IP Rating (Env) | P103 | IP | ≥ 54 | 54 |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 65 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Enclosure | IP Rating (Env) | P103 | IP | ≥ 54 | 54 |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 66 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Enclosure | IP Rating (Env) | P103 | IP | ≥ 54 | 54 |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 54 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Corrosion Protection | P104 |  | C4/C5 |  |  |  | Text | 3 | NO | DemoVolt PCS-A | DV-2500-L | C5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Corrosion Protection | P104 |  | C4/C5 |  |  |  | Text | 3 | NO | GridCore PCS-B | GC-2500-A | C4 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Corrosion Protection | P104 |  | C4/C5 |  |  |  | Text | 3 | NO | PowerStack PCS-C | PS-2200-L | C4 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Salt Mist Resistance | P105 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Salt Mist Resistance | P105 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Thermal & Environmental | Env | Salt Mist Resistance | P105 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Protection & Safety | Protection | AC Overvoltage Protection | P106 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | AC Overvoltage Protection | P106 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | AC Overvoltage Protection | P106 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | AC Undervoltage Protection | P107 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | AC Undervoltage Protection | P107 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | AC Undervoltage Protection | P107 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | DC Overvoltage Protection | P108 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | DC Overvoltage Protection | P108 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | DC Overvoltage Protection | P108 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | DC Undervoltage Protection | P109 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | DC Undervoltage Protection | P109 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | DC Undervoltage Protection | P109 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Overcurrent Protection | P110 |  | YES |  |  |  | Boolean | 4 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Overcurrent Protection | P110 |  | YES |  |  |  | Boolean | 4 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Overcurrent Protection | P110 |  | YES |  |  |  | Boolean | 4 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Short Circuit Protection | P111 |  | YES |  |  |  | Boolean | 4 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Short Circuit Protection | P111 |  | YES |  |  |  | Boolean | 4 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Short Circuit Protection | P111 |  | YES |  |  |  | Boolean | 4 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Overtemperature Protection | P112 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Overtemperature Protection | P112 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Overtemperature Protection | P112 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Insulation Monitoring | P113 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Insulation Monitoring | P113 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Insulation Monitoring | P113 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Ground Fault Protection | P114 |  | YES |  |  |  | Boolean | 4 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Ground Fault Protection | P114 |  | YES |  |  |  | Boolean | 4 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Ground Fault Protection | P114 |  | YES |  |  |  | Boolean | 4 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Anti-Islanding | P115 |  | YES |  |  |  | Boolean | 4 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Anti-Islanding | P115 |  | YES |  |  |  | Boolean | 4 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Anti-Islanding | P115 |  | YES |  |  |  | Boolean | 4 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | SPD | P116 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | SPD | P116 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | SPD | P116 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Emergency Stop | P117 |  | YES |  |  |  | Boolean | 4 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Emergency Stop | P117 |  | YES |  |  |  | Boolean | 4 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Emergency Stop | P117 |  | YES |  |  |  | Boolean | 4 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Fire System Interlock | P118 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Fire System Interlock | P118 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Fire System Interlock | P118 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | BMS Interlock | P119 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | BMS Interlock | P119 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | BMS Interlock | P119 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | EMS Interlock | P120 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | EMS Interlock | P120 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | EMS Interlock | P120 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | HVAC Interlock | P121 |  | YES |  |  |  | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | HVAC Interlock | P121 |  | YES |  |  |  | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | HVAC Interlock | P121 |  | YES |  |  |  | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Arc Fault Detection | P122 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | Arc Fault Detection | P122 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Protection & Safety | Protection | Arc Fault Detection | P122 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Protection & Safety | Protection | SPD Type | P123 |  | Type I+II |  |  |  | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Protection & Safety | Protection | SPD Type | P123 |  | Type I+II |  |  |  | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Protection & Safety | Protection | SPD Type | P123 |  | Type I+II |  |  |  | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Communication & Control | Comms | CAN | P124 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | CAN | P124 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | CAN | P124 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Modbus TCP | P125 |  | YES |  |  |  | Boolean | 4 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Modbus TCP | P125 |  | YES |  |  |  | Boolean | 4 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Modbus TCP | P125 |  | YES |  |  |  | Boolean | 4 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Modbus RTU | P126 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Modbus RTU | P126 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Modbus RTU | P126 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | IEC 61850 | P127 |  | YES |  |  |  | Boolean | 4 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | IEC 61850 | P127 |  | YES |  |  |  | Boolean | 4 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | IEC 61850 | P127 |  | YES |  |  |  | Boolean | 4 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | IEC 60870-5-104 | P128 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | IEC 60870-5-104 | P128 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | IEC 60870-5-104 | P128 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Ethernet | P129 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Ethernet | P129 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Ethernet | P129 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Fiber Optic | P130 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Fiber Optic | P130 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Fiber Optic | P130 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | SCADA Interface | P131 |  | YES |  |  |  | Boolean | 4 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | SCADA Interface | P131 |  | YES |  |  |  | Boolean | 4 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | SCADA Interface | P131 |  | YES |  |  |  | Boolean | 4 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | EMS Interface | P132 |  | YES |  |  |  | Boolean | 4 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | EMS Interface | P132 |  | YES |  |  |  | Boolean | 4 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | EMS Interface | P132 |  | YES |  |  |  | Boolean | 4 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | BMS Interface | P133 |  | YES |  |  |  | Boolean | 5 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | BMS Interface | P133 |  | YES |  |  |  | Boolean | 5 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | BMS Interface | P133 |  | YES |  |  |  | Boolean | 5 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Remote Monitoring | P134 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Remote Monitoring | P134 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Remote Monitoring | P134 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Remote Firmware Update | P135 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Remote Firmware Update | P135 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Remote Firmware Update | P135 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | NTP | P136 |  | YES |  |  |  | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | NTP | P136 |  | YES |  |  |  | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | NTP | P136 |  | YES |  |  |  | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | PTP | P137 |  | YES |  |  |  | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | PTP | P137 |  | YES |  |  |  | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | PTP | P137 |  | YES |  |  |  | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | GPS Time Synchronization | P138 |  | YES |  |  |  | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | GPS Time Synchronization | P138 |  | YES |  |  |  | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | GPS Time Synchronization | P138 |  | YES |  |  |  | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Cybersecurity Features | P139 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Cybersecurity Features | P139 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Communication & Control | Comms | Cybersecurity Features | P139 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Communication & Control | Comms | CAN Protocol | P140 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Communication & Control | Comms | CAN Protocol | P140 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Communication & Control | Comms | CAN Protocol | P140 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Mechanical | Dim | Length | P141 | mm |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Mechanical | Dim | Length | P141 | mm |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Mechanical | Dim | Length | P141 | mm |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Mechanical | Dim | Width | P142 | mm |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Mechanical | Dim | Width | P142 | mm |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Mechanical | Dim | Width | P142 | mm |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Mechanical | Dim | Height | P143 | mm |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Mechanical | Dim | Height | P143 | mm |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Mechanical | Dim | Height | P143 | mm |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Mechanical | Dim | Weight | P144 | kg |  |  |  |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 3200 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Dim | Weight | P144 | kg |  |  |  |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 3500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Dim | Weight | P144 | kg |  |  |  |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 2900 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Dim | Footprint | P145 | m² |  |  |  |  | Lower_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 4.2 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Dim | Footprint | P145 | m² |  |  |  |  | Lower_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 4.8 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Dim | Footprint | P145 | m² |  |  |  |  | Lower_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 3.9 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Mounting Method | P146 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Mechanical | Access | Mounting Method | P146 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Mechanical | Access | Mounting Method | P146 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Mechanical | Access | DC Cable Entry | P147 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Mechanical | Access | DC Cable Entry | P147 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Mechanical | Access | DC Cable Entry | P147 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Mechanical | Access | AC Cable Entry | P148 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Mechanical | Access | AC Cable Entry | P148 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Mechanical | Access | AC Cable Entry | P148 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Mechanical | Access | Top Cable Entry | P149 | [5 empty] | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Top Cable Entry | P149 | [5 empty] | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Top Cable Entry | P149 | [5 empty] | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Bottom Cable Entry | P150 | [5 empty] | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Bottom Cable Entry | P150 | [5 empty] | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Bottom Cable Entry | P150 | [5 empty] | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Front Access | P151 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Front Access | P151 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Front Access | P151 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Rear Access | P152 | [5 empty] | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Rear Access | P152 | [5 empty] | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Rear Access | P152 | [5 empty] | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Side Access | P153 | [5 empty] | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Side Access | P153 | [5 empty] | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Side Access | P153 | [5 empty] | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Access | Maintenance Clearance | P154 | mm |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Mechanical | Access | Maintenance Clearance | P154 | mm |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Mechanical | Access | Maintenance Clearance | P154 | mm |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Mechanical | Calc | Footprint per MW | P155 | m²/MW |  |  |  |  | Lower_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 1.68 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Calc | Footprint per MW | P155 | m²/MW |  |  |  |  | Lower_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 1.92 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Calc | Footprint per MW | P155 | m²/MW |  |  |  |  | Lower_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 1.77 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Calc | Weight per MW | P156 | kg/MW |  |  |  |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 1280 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Calc | Weight per MW | P156 | kg/MW |  |  |  |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 1400 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Mechanical | Calc | Weight per MW | P156 | kg/MW |  |  |  |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 1318 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | Design Life | P157 | years | ≥ 20 | 20 |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 25 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | Design Life | P157 | years | ≥ 20 | 20 |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 20 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | Design Life | P157 | years | ≥ 20 | 20 |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 20 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | Expected Service Life | P158 | years | ≥ 20 | 20 |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 25 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | Expected Service Life | P158 | years | ≥ 20 | 20 |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 20 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | Expected Service Life | P158 | years | ≥ 20 | 20 |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 20 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | MTBF | P159 | hours |  |  |  |  | Higher_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 200000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | MTBF | P159 | hours |  |  |  |  | Higher_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 150000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Life | MTBF | P159 | hours |  |  |  |  | Higher_Better | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Warranty | Warranty | P160 | years | ≥ 5 | 5 |  | 5 | Higher_Better | 4 | NO | DemoVolt PCS-A | DV-2500-L | 5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Warranty | Warranty | P160 | years | ≥ 5 | 5 |  | 5 | Higher_Better | 4 | NO | GridCore PCS-B | GC-2500-A | 5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Warranty | Warranty | P160 | years | ≥ 5 | 5 |  | 5 | Higher_Better | 4 | NO | PowerStack PCS-C | PS-2200-L | 5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Maint | Preventive Maintenance Interval | P161 | months |  |  |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Preventive Maintenance Interval | P161 | months |  |  |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Preventive Maintenance Interval | P161 | months |  |  |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Fan Life | P162 | hours |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Fan Life | P162 | hours |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Fan Life | P162 | hours |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Capacitor Life | P163 | hours |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Capacitor Life | P163 | hours |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Capacitor Life | P163 | hours |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Cooling System Life | P164 | years |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Cooling System Life | P164 | years |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Cooling System Life | P164 | years |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Filter Replacement Interval | P165 | months |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Filter Replacement Interval | P165 | months |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Filter Replacement Interval | P165 | months |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Major Component Replacement | P166 | years |  |  |  |  | Higher_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Major Component Replacement | P166 | years |  |  |  |  | Higher_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Reliability & Lifecycle | Maint | Major Component Replacement | P166 | years |  |  |  |  | Higher_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Service | Spare Parts Availability | P167 | [5 empty] | Text | 3 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Service | Spare Parts Availability | P167 | [5 empty] | Text | 3 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Reliability & Lifecycle | Service | Spare Parts Availability | P167 | [5 empty] | Text | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Reliability & Lifecycle | Service | Local Service Support | P168 |  | YES |  |  |  | Boolean | 4 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Service | Local Service Support | P168 |  | YES |  |  |  | Boolean | 4 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Service | Local Service Support | P168 |  | YES |  |  |  | Boolean | 4 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Service | Local Service Engineer | P169 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Service | Local Service Engineer | P169 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Service | Local Service Engineer | P169 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Service | India Stock Availability | P170 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Service | India Stock Availability | P170 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Reliability & Lifecycle | Service | India Stock Availability | P170 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62477-1 | P171 |  | YES |  |  |  | Boolean | 5 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62477-1 | P171 |  | YES |  |  |  | Boolean | 5 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62477-1 | P171 |  | YES |  |  |  | Boolean | 5 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 61000 Series | P172 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 61000 Series | P172 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 61000 Series | P172 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62109 | P173 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62109 | P173 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62109 | P173 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62933 | P174 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62933 | P174 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEC 62933 | P174 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 | P175 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 | P175 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 | P175 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 SA | P176 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 SA | P176 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 SA | P176 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 SB | P177 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 SB | P177 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 1741 SB | P177 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 9540 | P178 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 9540 | P178 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | UL 9540 | P178 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEEE 1547 | P179 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEEE 1547 | P179 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEEE 1547 | P179 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEEE 519 | P180 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEEE 519 | P180 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | IEEE 519 | P180 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | CE | P181 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | CE | P181 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | CE | P181 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | EMC | P182 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | EMC | P182 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | EMC | P182 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | Grid Code Compliance | P183 |  | YES |  |  |  | Boolean | 5 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | Grid Code Compliance | P183 |  | YES |  |  |  | Boolean | 5 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | Grid Code Compliance | P183 |  | YES |  |  |  | Boolean | 5 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | BIS | P184 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | BIS | P184 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Certification & Compliance | Cert | BIS | P184 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Certification & Compliance | Cert | Applicable Indian Standards | P185 |  | CEA 2022 |  |  |  | Text | 3 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Certification & Compliance | Cert | Applicable Indian Standards | P185 |  | CEA 2022 |  |  |  | Text | 3 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Certification & Compliance | Cert | Applicable Indian Standards | P185 |  | CEA 2022 |  |  |  | Text | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Number | P186 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Number | P186 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Number | P186 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Scope | P187 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Scope | P187 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Scope | P187 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Expiry Date | P188 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Expiry Date | P188 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Certification & Compliance | Cert | Certificate Expiry Date | P188 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
BESS Integration | BESS | BMS Compatibility | P189 |  | YES |  |  |  | Boolean | 5 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | BMS Compatibility | P189 |  | YES |  |  |  | Boolean | 5 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | BMS Compatibility | P189 |  | YES |  |  |  | Boolean | 5 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | EMS Compatibility | P190 |  | YES |  |  |  | Boolean | 5 | YES | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | EMS Compatibility | P190 |  | YES |  |  |  | Boolean | 5 | YES | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | EMS Compatibility | P190 |  | YES |  |  |  | Boolean | 5 | YES | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Battery Voltage Compatibility | P191 | [5 empty] | Text | 4 | YES | DemoVolt PCS-A | DV-2500-L | 1000-1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Battery Voltage Compatibility | P191 | [5 empty] | Text | 4 | YES | GridCore PCS-B | GC-2500-A | 1000-1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Battery Voltage Compatibility | P191 | [5 empty] | Text | 4 | YES | PowerStack PCS-C | PS-2200-L | 1100-1500 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Battery Current Compatibility | P192 | [5 empty] | Text | 3 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
BESS Integration | BESS | Battery Current Compatibility | P192 | [5 empty] | Text | 3 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
BESS Integration | BESS | Battery Current Compatibility | P192 | [5 empty] | Text | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
BESS Integration | BESS | SOC Communication | P193 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | SOC Communication | P193 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | SOC Communication | P193 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | SOH Communication | P194 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | SOH Communication | P194 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | SOH Communication | P194 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Charge Command | P195 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Charge Command | P195 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Charge Command | P195 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Discharge Command | P196 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Discharge Command | P196 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Discharge Command | P196 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Active Power Command | P197 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Active Power Command | P197 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Active Power Command | P197 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Reactive Power Command | P198 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Reactive Power Command | P198 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Reactive Power Command | P198 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Fast Power Response | P199 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Fast Power Response | P199 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Fast Power Response | P199 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Pre-charge Sequence | P200 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Pre-charge Sequence | P200 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Pre-charge Sequence | P200 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Contactor Control | P201 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Contactor Control | P201 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Contactor Control | P201 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | E-stop Integration | P202 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | E-stop Integration | P202 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | E-stop Integration | P202 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Fire Alarm Integration | P203 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Fire Alarm Integration | P203 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Fire Alarm Integration | P203 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | NO |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | HVAC Interlock | P204 |  | YES |  |  |  | Boolean | 1 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | HVAC Interlock | P204 |  | YES |  |  |  | Boolean | 1 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | HVAC Interlock | P204 |  | YES |  |  |  | Boolean | 1 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Rack Communication | P205 |  | YES |  |  |  | Boolean | 2 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Rack Communication | P205 |  | YES |  |  |  | Boolean | 2 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | Rack Communication | P205 |  | YES |  |  |  | Boolean | 2 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | DC Bus Compatibility | P206 |  | YES |  |  |  | Boolean | 3 | NO | DemoVolt PCS-A | DV-2500-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | DC Bus Compatibility | P206 |  | YES |  |  |  | Boolean | 3 | NO | GridCore PCS-B | GC-2500-A | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
BESS Integration | BESS | DC Bus Compatibility | P206 |  | YES |  |  |  | Boolean | 3 | NO | PowerStack PCS-C | PS-2200-L | YES |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | PCS Price | P207 | ₹ |  |  |  |  | Lower_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 9500000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | PCS Price | P207 | ₹ |  |  |  |  | Lower_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 9000000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | PCS Price | P207 | ₹ |  |  |  |  | Lower_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 8200000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | Price Currency | P208 | [5 empty] | Text | 1 | NO | DemoVolt PCS-A | DV-2500-L | INR |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | Price Currency | P208 | [5 empty] | Text | 1 | NO | GridCore PCS-B | GC-2500-A | INR |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | Price Currency | P208 | [5 empty] | Text | 1 | NO | PowerStack PCS-C | PS-2200-L | INR |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | Price per kW | P209 | ₹/kW |  |  |  |  | Lower_Better | 4 | NO | DemoVolt PCS-A | DV-2500-L | 3800 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | Price per kW | P209 | ₹/kW |  |  |  |  | Lower_Better | 4 | NO | GridCore PCS-B | GC-2500-A | 3600 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | Price per kW | P209 | ₹/kW |  |  |  |  | Lower_Better | 4 | NO | PowerStack PCS-C | PS-2200-L | 3727 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Price | Price per MW | P210 | ₹/MW |  |  |  |  | Lower_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Commercial | Price | Price per MW | P210 | ₹/MW |  |  |  |  | Lower_Better | 3 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Commercial | Price | Price per MW | P210 | ₹/MW |  |  |  |  | Lower_Better | 3 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Commercial | Cost | Installation Cost | P211 | ₹ |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Commercial | Cost | Installation Cost | P211 | ₹ |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Commercial | Cost | Installation Cost | P211 | ₹ |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Commercial | Cost | Commissioning Cost | P212 | ₹ |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Commercial | Cost | Commissioning Cost | P212 | ₹ |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Commercial | Cost | Commissioning Cost | P212 | ₹ |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Commercial | Cost | AMC Cost | P213 | ₹ |  |  |  |  | Lower_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Commercial | Cost | AMC Cost | P213 | ₹ |  |  |  |  | Lower_Better | 2 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Commercial | Cost | AMC Cost | P213 | ₹ |  |  |  |  | Lower_Better | 2 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Commercial | Warranty | Warranty Years | P214 | years | ≥ 5 | 5 |  |  | Higher_Better | 2 | NO | DemoVolt PCS-A | DV-2500-L | 5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Warranty | Warranty Years | P214 | years | ≥ 5 | 5 |  |  | Higher_Better | 2 | NO | GridCore PCS-B | GC-2500-A | 5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Warranty | Warranty Years | P214 | years | ≥ 5 | 5 |  |  | Higher_Better | 2 | NO | PowerStack PCS-C | PS-2200-L | 5 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Cost | Extended Warranty Cost | P215 | ₹ |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Commercial | Cost | Extended Warranty Cost | P215 | ₹ |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Commercial | Cost | Extended Warranty Cost | P215 | ₹ |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Commercial | Cost | Spare Parts Cost | P216 | ₹ |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Commercial | Cost | Spare Parts Cost | P216 | ₹ |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Commercial | Cost | Spare Parts Cost | P216 | ₹ |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Commercial | Cost | Transportation Cost | P217 | ₹ |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Commercial | Cost | Transportation Cost | P217 | ₹ |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Commercial | Cost | Transportation Cost | P217 | ₹ |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Commercial | Cost | Taxes/Duties | P218 | ₹ |  |  |  |  | Lower_Better | 1 | NO | DemoVolt PCS-A | DV-2500-L |  |  |  |  | Data Pending
Commercial | Cost | Taxes/Duties | P218 | ₹ |  |  |  |  | Lower_Better | 1 | NO | GridCore PCS-B | GC-2500-A |  |  |  |  | Data Pending
Commercial | Cost | Taxes/Duties | P218 | ₹ |  |  |  |  | Lower_Better | 1 | NO | PowerStack PCS-C | PS-2200-L |  |  |  |  | Data Pending
Commercial | Cost | Total Delivered Cost | P219 | ₹ |  |  |  |  | Lower_Better | 3 | NO | DemoVolt PCS-A | DV-2500-L | 10200000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Cost | Total Delivered Cost | P219 | ₹ |  |  |  |  | Lower_Better | 3 | NO | GridCore PCS-B | GC-2500-A | 9700000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Cost | Total Delivered Cost | P219 | ₹ |  |  |  |  | Lower_Better | 3 | NO | PowerStack PCS-C | PS-2200-L | 8900000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Calc | Total Cost per MW | P220 | ₹/MW |  |  |  |  | Lower_Better | 4 | NO | DemoVolt PCS-A | DV-2500-L | 4080000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Calc | Total Cost per MW | P220 | ₹/MW |  |  |  |  | Lower_Better | 4 | NO | GridCore PCS-B | GC-2500-A | 3880000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
Commercial | Calc | Total Cost per MW | P220 | ₹/MW |  |  |  |  | Lower_Better | 4 | NO | PowerStack PCS-C | PS-2200-L | 4045000 |  | Sample/Demo | 2026-08-01 | DEMO DATA — not real specs
↑ Yellow column = enter vendor values here. Rows shown are DEMO data — replace with real datasheet values.

## Requirements
Parameter_ID | Category | Parameter | Unit | Requirement | Req_Min | Req_Max | Preferred | Comparison_Type | Critical
P001 | Basic Configuration | PCS Type |  | Central/String |  |  |  | Text | NO
P002 | Basic Configuration | PCS Architecture |  | Modular preferred |  |  |  | Text | NO
P003 | Basic Configuration | Rated Power | kW | ≥ 2500 | 2500 |  | 2500 | Higher_Better | YES
P004 | Basic Configuration | Maximum Power | kW | ≥ 2500 | 2500 |  |  | Higher_Better | NO
P005 | Basic Configuration | Continuous Power | kW | ≥ 2500 | 2500 |  |  | Higher_Better | NO
P006 | Basic Configuration | Modular/Standalone |  | Modular |  |  |  | Text | NO
P007 | Basic Configuration | Number of Power Modules | nos |  |  |  |  | Higher_Better | NO
P008 | Basic Configuration | Parallel PCS Capability |  | YES |  |  |  | Boolean | NO
P009 | Basic Configuration | Transformer Requirement | [5 empty] | Text | NO
P010 | Basic Configuration | Transformer Integrated | [5 empty] | Boolean | NO
P011 | Basic Configuration | Cooling Type |  | Liquid/Forced air |  |  |  | Text | NO
P012 | Basic Configuration | IP Rating | IP | ≥ 54 | 54 |  | 65 | Higher_Better | NO
P013 | Basic Configuration | Installation Type | [5 empty] | Text | NO
P014 | Basic Configuration | Indoor/Outdoor |  | Outdoor |  |  |  | Text | NO
P015 | DC Electrical | Minimum DC Voltage | V | ≤ 1000 |  | 1000 |  | Lower_Better | YES
P016 | DC Electrical | Nominal DC Voltage | V |  |  |  |  | Range | NO
P017 | DC Electrical | Maximum DC Voltage | V | ≥ 1500 | 1500 |  | 1500 | Higher_Better | YES
P018 | DC Electrical | DC Operating Voltage Range | V | 1000-1500 | 1000 | 1500 |  | Range | YES
P019 | DC Electrical | Rated DC Current | A |  |  |  |  | Higher_Better | NO
P020 | DC Electrical | Maximum DC Current | A |  |  |  |  | Higher_Better | YES
P021 | DC Electrical | Continuous DC Current | A |  |  |  |  | Higher_Better | NO
P022 | DC Electrical | DC Overload Current | A |  |  |  |  | Higher_Better | NO
P023 | DC Electrical | DC Ripple Current | % | ≤ 3 |  | 3 |  | Lower_Better | NO
P024 | DC Electrical | DC Voltage Accuracy | % | ≤ 1 |  | 1 |  | Lower_Better | NO
P025 | DC Electrical | DC Current Accuracy | % | ≤ 1 |  | 1 |  | Lower_Better | NO
P026 | DC Electrical | DC Isolation |  | YES |  |  |  | Boolean | NO
P027 | DC Electrical | Insulation Monitoring |  | YES |  |  |  | Boolean | NO
P028 | DC Electrical | Reverse Polarity Protection |  | YES |  |  |  | Boolean | NO
P029 | DC Electrical | DC Contactor |  | YES |  |  |  | Boolean | NO
P030 | DC Electrical | Pre-charge Function |  | YES |  |  |  | Boolean | NO
P031 | DC Electrical | DC Fuse |  | YES |  |  |  | Boolean | NO
P032 | DC Electrical | Ground Fault Detection |  | YES |  |  |  | Boolean | NO
P033 | AC Electrical | Rated AC Power | kVA | ≥ 2500 | 2500 |  |  | Higher_Better | YES
P034 | AC Electrical | Maximum AC Power | kVA |  |  |  |  | Higher_Better | NO
P035 | AC Electrical | AC Voltage | V | 690 |  |  |  | Range | YES
P036 | AC Electrical | AC Voltage Range | V |  |  |  |  | Range | NO
P037 | AC Electrical | AC Frequency | Hz | 50 |  |  |  | Range | NO
P038 | AC Electrical | Frequency Range | Hz | 47.5-51.5 |  |  |  | Range | NO
P039 | AC Electrical | Rated AC Current | A |  |  |  |  | Higher_Better | NO
P040 | AC Electrical | Maximum AC Current | A |  |  |  |  | Higher_Better | NO
P041 | AC Electrical | Power Factor Range |  | -1 to +1 |  |  |  | Range | NO
P042 | AC Electrical | Reactive Power | kVAr |  |  |  |  | Higher_Better | NO
P043 | AC Electrical | Reactive Power at Rated Power | kVAr |  |  |  |  | Higher_Better | NO
P044 | AC Electrical | THDi | % | ≤ 3 |  | 3 | 2 | Lower_Better | NO
P045 | AC Electrical | DC Injection | % | ≤ 0.5 |  | 0.5 |  | Lower_Better | NO
P046 | AC Electrical | AC Voltage THD | % | ≤ 3 |  | 3 |  | Lower_Better | NO
P047 | AC Electrical | Three Phase |  | YES |  |  |  | Boolean | NO
P048 | AC Electrical | Grid Connection Type | [5 empty] | Text | NO
P049 | Performance & Efficiency | Maximum Efficiency | % | ≥ 99 | 99 |  | 99 | Higher_Better | NO
P050 | Performance & Efficiency | Efficiency @ 10% Load | % |  |  |  |  | Higher_Better | NO
P051 | Performance & Efficiency | Efficiency @ 25% Load | % |  |  |  |  | Higher_Better | NO
P052 | Performance & Efficiency | Efficiency @ 50% Load | % | ≥ 98 | 98 |  |  | Higher_Better | NO
P053 | Performance & Efficiency | Efficiency @ 75% Load | % |  |  |  |  | Higher_Better | NO
P054 | Performance & Efficiency | Efficiency @ 100% Load | % | ≥ 98 | 98 |  |  | Higher_Better | NO
P055 | Performance & Efficiency | European Efficiency | % | ≥ 98.5 | 98.5 |  |  | Higher_Better | NO
P056 | Performance & Efficiency | Weighted Efficiency | % |  |  |  |  | Higher_Better | NO
P057 | Performance & Efficiency | Standby Power | W |  |  |  |  | Lower_Better | NO
P058 | Performance & Efficiency | Standby Consumption | W |  |  |  |  | Lower_Better | NO
P059 | Performance & Efficiency | Night-time Consumption | W |  |  |  |  | Lower_Better | NO
P060 | Performance & Efficiency | Auxiliary Consumption | W |  |  |  |  | Lower_Better | NO
P061 | Overload Capability | 105% Overload Duration | s |  |  |  |  | Higher_Better | NO
P062 | Overload Capability | 110% Overload Duration | s | ≥ 60 | 60 |  |  | Higher_Better | NO
P063 | Overload Capability | 120% Overload Duration | s | ≥ 60 | 60 |  |  | Higher_Better | NO
P064 | Overload Capability | 125% Overload Duration | s |  |  |  |  | Higher_Better | NO
P065 | Overload Capability | 150% Overload Duration | s |  |  |  |  | Higher_Better | NO
P066 | Overload Capability | Maximum AC Current (Overload) | A |  |  |  |  | Higher_Better | NO
P067 | Overload Capability | Maximum DC Current (Overload) | A |  |  |  |  | Higher_Better | NO
P068 | Overload Capability | Short Circuit Current | A |  |  |  |  | Higher_Better | NO
P069 | Overload Capability | Fault Current Contribution | A |  |  |  |  | Higher_Better | NO
P070 | Grid Support | Grid Following |  | YES |  |  |  | Boolean | NO
P071 | Grid Support | Grid Forming |  | YES |  |  |  | Boolean | YES
P072 | Grid Support | LVRT |  | YES |  |  |  | Boolean | YES
P073 | Grid Support | HVRT |  | YES |  |  |  | Boolean | YES
P074 | Grid Support | Frequency Ride Through |  | YES |  |  |  | Boolean | NO
P075 | Grid Support | Active Power Control |  | YES |  |  |  | Boolean | NO
P076 | Grid Support | Reactive Power Control |  | YES |  |  |  | Boolean | NO
P077 | Grid Support | Volt-VAR |  | YES |  |  |  | Boolean | NO
P078 | Grid Support | Volt-Watt |  | YES |  |  |  | Boolean | NO
P079 | Grid Support | Frequency-Watt |  | YES |  |  |  | Boolean | NO
P080 | Grid Support | Droop Control |  | YES |  |  |  | Boolean | NO
P081 | Grid Support | Active Power Ramp Rate | %/s |  |  |  |  | Higher_Better | NO
P082 | Grid Support | Reactive Power Response Time | ms |  |  |  |  | Lower_Better | NO
P083 | Grid Support | Active Power Response Time | ms | ≤ 100 |  | 100 |  | Lower_Better | NO
P084 | Grid Support | Black Start |  | YES |  |  |  | Boolean | NO
P085 | Grid Support | Islanding Operation |  | YES |  |  |  | Boolean | NO
P086 | Grid Support | Synchronization Time | s |  |  |  |  | Lower_Better | NO
P087 | Grid Support | Virtual Synchronous Machine |  | YES |  |  |  | Boolean | NO
P088 | Grid Support | Synthetic Inertia |  | YES |  |  |  | Boolean | NO
P089 | Thermal & Environmental | Minimum Operating Temperature | °C | ≤ -20 |  | -20 |  | Lower_Better | NO
P090 | Thermal & Environmental | Maximum Operating Temperature | °C | ≥ 60 | 60 |  |  | Higher_Better | NO
P091 | Thermal & Environmental | Full Rated Power Temperature | °C | ≥ 50 | 50 |  | 55 | Higher_Better | YES
P092 | Thermal & Environmental | Derating Start Temperature | °C | ≥ 50 | 50 |  |  | Higher_Better | NO
P093 | Thermal & Environmental | Maximum Temperature | °C |  |  |  |  | Higher_Better | NO
P094 | Thermal & Environmental | Temperature Derating | %/°C |  |  |  |  | Lower_Better | NO
P095 | Thermal & Environmental | Minimum Storage Temperature | °C |  |  |  |  | Lower_Better | NO
P096 | Thermal & Environmental | Maximum Storage Temperature | °C |  |  |  |  | Higher_Better | NO
P097 | Thermal & Environmental | Relative Humidity | % | 0-100 |  |  |  | Range | NO
P098 | Thermal & Environmental | Maximum Altitude | m | ≥ 3000 | 3000 |  |  | Higher_Better | NO
P099 | Thermal & Environmental | Altitude Derating | [5 empty] | Text | NO
P100 | Thermal & Environmental | Cooling Type | [5 empty] | Text | NO
P101 | Thermal & Environmental | Cooling Power Consumption | W |  |  |  |  | Lower_Better | NO
P102 | Thermal & Environmental | Noise | dB | ≤ 80 |  | 80 |  | Lower_Better | NO
P103 | Thermal & Environmental | IP Rating (Env) | IP | ≥ 54 | 54 |  |  | Higher_Better | NO
P104 | Thermal & Environmental | Corrosion Protection |  | C4/C5 |  |  |  | Text | NO
P105 | Thermal & Environmental | Salt Mist Resistance |  | YES |  |  |  | Boolean | NO
P106 | Protection & Safety | AC Overvoltage Protection |  | YES |  |  |  | Boolean | NO
P107 | Protection & Safety | AC Undervoltage Protection |  | YES |  |  |  | Boolean | NO
P108 | Protection & Safety | DC Overvoltage Protection |  | YES |  |  |  | Boolean | NO
P109 | Protection & Safety | DC Undervoltage Protection |  | YES |  |  |  | Boolean | NO
P110 | Protection & Safety | Overcurrent Protection |  | YES |  |  |  | Boolean | YES
P111 | Protection & Safety | Short Circuit Protection |  | YES |  |  |  | Boolean | YES
P112 | Protection & Safety | Overtemperature Protection |  | YES |  |  |  | Boolean | NO
P113 | Protection & Safety | Insulation Monitoring |  | YES |  |  |  | Boolean | NO
P114 | Protection & Safety | Ground Fault Protection |  | YES |  |  |  | Boolean | YES
P115 | Protection & Safety | Anti-Islanding |  | YES |  |  |  | Boolean | YES
P116 | Protection & Safety | SPD |  | YES |  |  |  | Boolean | NO
P117 | Protection & Safety | Emergency Stop |  | YES |  |  |  | Boolean | YES
P118 | Protection & Safety | Fire System Interlock |  | YES |  |  |  | Boolean | NO
P119 | Protection & Safety | BMS Interlock |  | YES |  |  |  | Boolean | NO
P120 | Protection & Safety | EMS Interlock |  | YES |  |  |  | Boolean | NO
P121 | Protection & Safety | HVAC Interlock |  | YES |  |  |  | Boolean | NO
P122 | Protection & Safety | Arc Fault Detection |  | YES |  |  |  | Boolean | NO
P123 | Protection & Safety | SPD Type |  | Type I+II |  |  |  | Text | NO
P124 | Communication & Control | CAN |  | YES |  |  |  | Boolean | NO
P125 | Communication & Control | Modbus TCP |  | YES |  |  |  | Boolean | NO
P126 | Communication & Control | Modbus RTU |  | YES |  |  |  | Boolean | NO
P127 | Communication & Control | IEC 61850 |  | YES |  |  |  | Boolean | NO
P128 | Communication & Control | IEC 60870-5-104 |  | YES |  |  |  | Boolean | NO
P129 | Communication & Control | Ethernet |  | YES |  |  |  | Boolean | NO
P130 | Communication & Control | Fiber Optic |  | YES |  |  |  | Boolean | NO
P131 | Communication & Control | SCADA Interface |  | YES |  |  |  | Boolean | NO
P132 | Communication & Control | EMS Interface |  | YES |  |  |  | Boolean | YES
P133 | Communication & Control | BMS Interface |  | YES |  |  |  | Boolean | YES
P134 | Communication & Control | Remote Monitoring |  | YES |  |  |  | Boolean | NO
P135 | Communication & Control | Remote Firmware Update |  | YES |  |  |  | Boolean | NO
P136 | Communication & Control | NTP |  | YES |  |  |  | Boolean | NO
P137 | Communication & Control | PTP |  | YES |  |  |  | Boolean | NO
P138 | Communication & Control | GPS Time Synchronization |  | YES |  |  |  | Boolean | NO
P139 | Communication & Control | Cybersecurity Features |  | YES |  |  |  | Boolean | NO
P140 | Communication & Control | CAN Protocol | [5 empty] | Text | NO
P141 | Mechanical | Length | mm |  |  |  |  | Lower_Better | NO
P142 | Mechanical | Width | mm |  |  |  |  | Lower_Better | NO
P143 | Mechanical | Height | mm |  |  |  |  | Lower_Better | NO
P144 | Mechanical | Weight | kg |  |  |  |  | Lower_Better | NO
P145 | Mechanical | Footprint | m² |  |  |  |  | Lower_Better | NO
P146 | Mechanical | Mounting Method | [5 empty] | Text | NO
P147 | Mechanical | DC Cable Entry | [5 empty] | Text | NO
P148 | Mechanical | AC Cable Entry | [5 empty] | Text | NO
P149 | Mechanical | Top Cable Entry | [5 empty] | Boolean | NO
P150 | Mechanical | Bottom Cable Entry | [5 empty] | Boolean | NO
P151 | Mechanical | Front Access |  | YES |  |  |  | Boolean | NO
P152 | Mechanical | Rear Access | [5 empty] | Boolean | NO
P153 | Mechanical | Side Access | [5 empty] | Boolean | NO
P154 | Mechanical | Maintenance Clearance | mm |  |  |  |  | Lower_Better | NO
P155 | Mechanical | Footprint per MW | m²/MW |  |  |  |  | Lower_Better | NO
P156 | Mechanical | Weight per MW | kg/MW |  |  |  |  | Lower_Better | NO
P157 | Reliability & Lifecycle | Design Life | years | ≥ 20 | 20 |  |  | Higher_Better | NO
P158 | Reliability & Lifecycle | Expected Service Life | years | ≥ 20 | 20 |  |  | Higher_Better | NO
P159 | Reliability & Lifecycle | MTBF | hours |  |  |  |  | Higher_Better | NO
P160 | Reliability & Lifecycle | Warranty | years | ≥ 5 | 5 |  | 5 | Higher_Better | NO
P161 | Reliability & Lifecycle | Preventive Maintenance Interval | months |  |  |  |  | Higher_Better | NO
P162 | Reliability & Lifecycle | Fan Life | hours |  |  |  |  | Higher_Better | NO
P163 | Reliability & Lifecycle | Capacitor Life | hours |  |  |  |  | Higher_Better | NO
P164 | Reliability & Lifecycle | Cooling System Life | years |  |  |  |  | Higher_Better | NO
P165 | Reliability & Lifecycle | Filter Replacement Interval | months |  |  |  |  | Higher_Better | NO
P166 | Reliability & Lifecycle | Major Component Replacement | years |  |  |  |  | Higher_Better | NO
P167 | Reliability & Lifecycle | Spare Parts Availability | [5 empty] | Text | NO
P168 | Reliability & Lifecycle | Local Service Support |  | YES |  |  |  | Boolean | NO
P169 | Reliability & Lifecycle | Local Service Engineer |  | YES |  |  |  | Boolean | NO
P170 | Reliability & Lifecycle | India Stock Availability |  | YES |  |  |  | Boolean | NO
P171 | Certification & Compliance | IEC 62477-1 |  | YES |  |  |  | Boolean | YES
P172 | Certification & Compliance | IEC 61000 Series |  | YES |  |  |  | Boolean | NO
P173 | Certification & Compliance | IEC 62109 |  | YES |  |  |  | Boolean | NO
P174 | Certification & Compliance | IEC 62933 |  | YES |  |  |  | Boolean | NO
P175 | Certification & Compliance | UL 1741 |  | YES |  |  |  | Boolean | NO
P176 | Certification & Compliance | UL 1741 SA |  | YES |  |  |  | Boolean | NO
P177 | Certification & Compliance | UL 1741 SB |  | YES |  |  |  | Boolean | NO
P178 | Certification & Compliance | UL 9540 |  | YES |  |  |  | Boolean | NO
P179 | Certification & Compliance | IEEE 1547 |  | YES |  |  |  | Boolean | NO
P180 | Certification & Compliance | IEEE 519 |  | YES |  |  |  | Boolean | NO
P181 | Certification & Compliance | CE |  | YES |  |  |  | Boolean | NO
P182 | Certification & Compliance | EMC |  | YES |  |  |  | Boolean | NO
P183 | Certification & Compliance | Grid Code Compliance |  | YES |  |  |  | Boolean | YES
P184 | Certification & Compliance | BIS |  | YES |  |  |  | Boolean | NO
P185 | Certification & Compliance | Applicable Indian Standards |  | CEA 2022 |  |  |  | Text | NO
P186 | Certification & Compliance | Certificate Number | [5 empty] | Text | NO
P187 | Certification & Compliance | Certificate Scope | [5 empty] | Text | NO
P188 | Certification & Compliance | Certificate Expiry Date | [5 empty] | Text | NO
P189 | BESS Integration | BMS Compatibility |  | YES |  |  |  | Boolean | YES
P190 | BESS Integration | EMS Compatibility |  | YES |  |  |  | Boolean | YES
P191 | BESS Integration | Battery Voltage Compatibility | [5 empty] | Text | YES
P192 | BESS Integration | Battery Current Compatibility | [5 empty] | Text | NO
P193 | BESS Integration | SOC Communication |  | YES |  |  |  | Boolean | NO
P194 | BESS Integration | SOH Communication |  | YES |  |  |  | Boolean | NO
P195 | BESS Integration | Charge Command |  | YES |  |  |  | Boolean | NO
P196 | BESS Integration | Discharge Command |  | YES |  |  |  | Boolean | NO
P197 | BESS Integration | Active Power Command |  | YES |  |  |  | Boolean | NO
P198 | BESS Integration | Reactive Power Command |  | YES |  |  |  | Boolean | NO
P199 | BESS Integration | Fast Power Response |  | YES |  |  |  | Boolean | NO
P200 | BESS Integration | Pre-charge Sequence |  | YES |  |  |  | Boolean | NO
P201 | BESS Integration | Contactor Control |  | YES |  |  |  | Boolean | NO
P202 | BESS Integration | E-stop Integration |  | YES |  |  |  | Boolean | NO
P203 | BESS Integration | Fire Alarm Integration |  | YES |  |  |  | Boolean | NO
P204 | BESS Integration | HVAC Interlock |  | YES |  |  |  | Boolean | NO
P205 | BESS Integration | Rack Communication |  | YES |  |  |  | Boolean | NO
P206 | BESS Integration | DC Bus Compatibility |  | YES |  |  |  | Boolean | NO
P207 | Commercial | PCS Price | ₹ |  |  |  |  | Lower_Better | NO
P208 | Commercial | Price Currency | [5 empty] | Text | NO
P209 | Commercial | Price per kW | ₹/kW |  |  |  |  | Lower_Better | NO
P210 | Commercial | Price per MW | ₹/MW |  |  |  |  | Lower_Better | NO
P211 | Commercial | Installation Cost | ₹ |  |  |  |  | Lower_Better | NO
P212 | Commercial | Commissioning Cost | ₹ |  |  |  |  | Lower_Better | NO
P213 | Commercial | AMC Cost | ₹ |  |  |  |  | Lower_Better | NO
P214 | Commercial | Warranty Years | years | ≥ 5 | 5 |  |  | Higher_Better | NO
P215 | Commercial | Extended Warranty Cost | ₹ |  |  |  |  | Lower_Better | NO
P216 | Commercial | Spare Parts Cost | ₹ |  |  |  |  | Lower_Better | NO
P217 | Commercial | Transportation Cost | ₹ |  |  |  |  | Lower_Better | NO
P218 | Commercial | Taxes/Duties | ₹ |  |  |  |  | Lower_Better | NO
P219 | Commercial | Total Delivered Cost | ₹ |  |  |  |  | Lower_Better | NO
P220 | Commercial | Total Cost per MW | ₹/MW |  |  |  |  | Lower_Better | NO

## Parameter_Master
Parameter_ID | Category | Subcategory | Parameter | Unit | Comparison_Type | Weight | Critical
P001 | Basic Configuration | Type | PCS Type |  | Text | 2 | NO
P002 | Basic Configuration | Type | PCS Architecture |  | Text | 2 | NO
P003 | Basic Configuration | Power | Rated Power | kW | Higher_Better | 5 | YES
P004 | Basic Configuration | Power | Maximum Power | kW | Higher_Better | 3 | NO
P005 | Basic Configuration | Power | Continuous Power | kW | Higher_Better | 3 | NO
P006 | Basic Configuration | Config | Modular/Standalone |  | Text | 2 | NO
P007 | Basic Configuration | Config | Number of Power Modules | nos | Higher_Better | 1 | NO
P008 | Basic Configuration | Config | Parallel PCS Capability |  | Boolean | 3 | NO
P009 | Basic Configuration | Config | Transformer Requirement |  | Text | 2 | NO
P010 | Basic Configuration | Config | Transformer Integrated |  | Boolean | 1 | NO
P011 | Basic Configuration | Cooling | Cooling Type |  | Text | 3 | NO
P012 | Basic Configuration | Enclosure | IP Rating | IP | Higher_Better | 4 | NO
P013 | Basic Configuration | Install | Installation Type |  | Text | 1 | NO
P014 | Basic Configuration | Install | Indoor/Outdoor |  | Text | 2 | NO
P015 | DC Electrical | Voltage | Minimum DC Voltage | V | Lower_Better | 4 | YES
P016 | DC Electrical | Voltage | Nominal DC Voltage | V | Range | 2 | NO
P017 | DC Electrical | Voltage | Maximum DC Voltage | V | Higher_Better | 4 | YES
P018 | DC Electrical | Voltage | DC Operating Voltage Range | V | Range | 5 | YES
P019 | DC Electrical | Current | Rated DC Current | A | Higher_Better | 3 | NO
P020 | DC Electrical | Current | Maximum DC Current | A | Higher_Better | 3 | YES
P021 | DC Electrical | Current | Continuous DC Current | A | Higher_Better | 2 | NO
P022 | DC Electrical | Current | DC Overload Current | A | Higher_Better | 2 | NO
P023 | DC Electrical | Quality | DC Ripple Current | % | Lower_Better | 2 | NO
P024 | DC Electrical | Accuracy | DC Voltage Accuracy | % | Lower_Better | 1 | NO
P025 | DC Electrical | Accuracy | DC Current Accuracy | % | Lower_Better | 1 | NO
P026 | DC Electrical | Protection | DC Isolation |  | Boolean | 2 | NO
P027 | DC Electrical | Protection | Insulation Monitoring |  | Boolean | 3 | NO
P028 | DC Electrical | Protection | Reverse Polarity Protection |  | Boolean | 3 | NO
P029 | DC Electrical | Protection | DC Contactor |  | Boolean | 2 | NO
P030 | DC Electrical | Protection | Pre-charge Function |  | Boolean | 2 | NO
P031 | DC Electrical | Protection | DC Fuse |  | Boolean | 1 | NO
P032 | DC Electrical | Protection | Ground Fault Detection |  | Boolean | 3 | NO
P033 | AC Electrical | Power | Rated AC Power | kVA | Higher_Better | 5 | YES
P034 | AC Electrical | Power | Maximum AC Power | kVA | Higher_Better | 3 | NO
P035 | AC Electrical | Voltage | AC Voltage | V | Range | 4 | YES
P036 | AC Electrical | Voltage | AC Voltage Range | V | Range | 3 | NO
P037 | AC Electrical | Freq | AC Frequency | Hz | Range | 3 | NO
P038 | AC Electrical | Freq | Frequency Range | Hz | Range | 2 | NO
P039 | AC Electrical | Current | Rated AC Current | A | Higher_Better | 2 | NO
P040 | AC Electrical | Current | Maximum AC Current | A | Higher_Better | 2 | NO
P041 | AC Electrical | PF | Power Factor Range |  | Range | 3 | NO
P042 | AC Electrical | Reactive | Reactive Power | kVAr | Higher_Better | 2 | NO
P043 | AC Electrical | Reactive | Reactive Power at Rated Power | kVAr | Higher_Better | 2 | NO
P044 | AC Electrical | Quality | THDi | % | Lower_Better | 4 | NO
P045 | AC Electrical | Quality | DC Injection | % | Lower_Better | 2 | NO
P046 | AC Electrical | Quality | AC Voltage THD | % | Lower_Better | 2 | NO
P047 | AC Electrical | Config | Three Phase |  | Boolean | 1 | NO
P048 | AC Electrical | Config | Grid Connection Type |  | Text | 1 | NO
P049 | Performance & Efficiency | Efficiency | Maximum Efficiency | % | Higher_Better | 5 | NO
P050 | Performance & Efficiency | Efficiency | Efficiency @ 10% Load | % | Higher_Better | 1 | NO
P051 | Performance & Efficiency | Efficiency | Efficiency @ 25% Load | % | Higher_Better | 2 | NO
P052 | Performance & Efficiency | Efficiency | Efficiency @ 50% Load | % | Higher_Better | 4 | NO
P053 | Performance & Efficiency | Efficiency | Efficiency @ 75% Load | % | Higher_Better | 2 | NO
P054 | Performance & Efficiency | Efficiency | Efficiency @ 100% Load | % | Higher_Better | 3 | NO
P055 | Performance & Efficiency | Efficiency | European Efficiency | % | Higher_Better | 4 | NO
P056 | Performance & Efficiency | Efficiency | Weighted Efficiency | % | Higher_Better | 2 | NO
P057 | Performance & Efficiency | Aux | Standby Power | W | Lower_Better | 2 | NO
P058 | Performance & Efficiency | Aux | Standby Consumption | W | Lower_Better | 1 | NO
P059 | Performance & Efficiency | Aux | Night-time Consumption | W | Lower_Better | 1 | NO
P060 | Performance & Efficiency | Aux | Auxiliary Consumption | W | Lower_Better | 2 | NO
P061 | Overload Capability | Overload | 105% Overload Duration | s | Higher_Better | 1 | NO
P062 | Overload Capability | Overload | 110% Overload Duration | s | Higher_Better | 3 | NO
P063 | Overload Capability | Overload | 120% Overload Duration | s | Higher_Better | 2 | NO
P064 | Overload Capability | Overload | 125% Overload Duration | s | Higher_Better | 1 | NO
P065 | Overload Capability | Overload | 150% Overload Duration | s | Higher_Better | 1 | NO
P066 | Overload Capability | Current | Maximum AC Current (Overload) | A | Higher_Better | 2 | NO
P067 | Overload Capability | Current | Maximum DC Current (Overload) | A | Higher_Better | 2 | NO
P068 | Overload Capability | Fault | Short Circuit Current | A | Higher_Better | 2 | NO
P069 | Overload Capability | Fault | Fault Current Contribution | A | Higher_Better | 2 | NO
P070 | Grid Support | Mode | Grid Following |  | Boolean | 3 | NO
P071 | Grid Support | Mode | Grid Forming |  | Boolean | 5 | YES
P072 | Grid Support | RideThrough | LVRT |  | Boolean | 5 | YES
P073 | Grid Support | RideThrough | HVRT |  | Boolean | 4 | YES
P074 | Grid Support | RideThrough | Frequency Ride Through |  | Boolean | 3 | NO
P075 | Grid Support | Control | Active Power Control |  | Boolean | 3 | NO
P076 | Grid Support | Control | Reactive Power Control |  | Boolean | 3 | NO
P077 | Grid Support | Control | Volt-VAR |  | Boolean | 2 | NO
P078 | Grid Support | Control | Volt-Watt |  | Boolean | 2 | NO
P079 | Grid Support | Control | Frequency-Watt |  | Boolean | 2 | NO
P080 | Grid Support | Control | Droop Control |  | Boolean | 2 | NO
P081 | Grid Support | Dynamic | Active Power Ramp Rate | %/s | Higher_Better | 2 | NO
P082 | Grid Support | Dynamic | Reactive Power Response Time | ms | Lower_Better | 2 | NO
P083 | Grid Support | Dynamic | Active Power Response Time | ms | Lower_Better | 3 | NO
P084 | Grid Support | Advanced | Black Start |  | Boolean | 3 | NO
P085 | Grid Support | Advanced | Islanding Operation |  | Boolean | 2 | NO
P086 | Grid Support | Advanced | Synchronization Time | s | Lower_Better | 1 | NO
P087 | Grid Support | Advanced | Virtual Synchronous Machine |  | Boolean | 2 | NO
P088 | Grid Support | Advanced | Synthetic Inertia |  | Boolean | 2 | NO
P089 | Thermal & Environmental | Temp | Minimum Operating Temperature | °C | Lower_Better | 2 | NO
P090 | Thermal & Environmental | Temp | Maximum Operating Temperature | °C | Higher_Better | 2 | NO
P091 | Thermal & Environmental | Temp | Full Rated Power Temperature | °C | Higher_Better | 5 | YES
P092 | Thermal & Environmental | Temp | Derating Start Temperature | °C | Higher_Better | 4 | NO
P093 | Thermal & Environmental | Temp | Maximum Temperature | °C | Higher_Better | 1 | NO
P094 | Thermal & Environmental | Temp | Temperature Derating | %/°C | Lower_Better | 2 | NO
P095 | Thermal & Environmental | Storage | Minimum Storage Temperature | °C | Lower_Better | 1 | NO
P096 | Thermal & Environmental | Storage | Maximum Storage Temperature | °C | Higher_Better | 1 | NO
P097 | Thermal & Environmental | Env | Relative Humidity | % | Range | 2 | NO
P098 | Thermal & Environmental | Env | Maximum Altitude | m | Higher_Better | 3 | NO
P099 | Thermal & Environmental | Env | Altitude Derating |  | Text | 1 | NO
P100 | Thermal & Environmental | Cooling | Cooling Type |  | Text | 2 | NO
P101 | Thermal & Environmental | Cooling | Cooling Power Consumption | W | Lower_Better | 1 | NO
P102 | Thermal & Environmental | Env | Noise | dB | Lower_Better | 2 | NO
P103 | Thermal & Environmental | Enclosure | IP Rating (Env) | IP | Higher_Better | 3 | NO
P104 | Thermal & Environmental | Env | Corrosion Protection |  | Text | 3 | NO
P105 | Thermal & Environmental | Env | Salt Mist Resistance |  | Boolean | 2 | NO
P106 | Protection & Safety | Protection | AC Overvoltage Protection |  | Boolean | 3 | NO
P107 | Protection & Safety | Protection | AC Undervoltage Protection |  | Boolean | 3 | NO
P108 | Protection & Safety | Protection | DC Overvoltage Protection |  | Boolean | 3 | NO
P109 | Protection & Safety | Protection | DC Undervoltage Protection |  | Boolean | 3 | NO
P110 | Protection & Safety | Protection | Overcurrent Protection |  | Boolean | 4 | YES
P111 | Protection & Safety | Protection | Short Circuit Protection |  | Boolean | 4 | YES
P112 | Protection & Safety | Protection | Overtemperature Protection |  | Boolean | 3 | NO
P113 | Protection & Safety | Protection | Insulation Monitoring |  | Boolean | 3 | NO
P114 | Protection & Safety | Protection | Ground Fault Protection |  | Boolean | 4 | YES
P115 | Protection & Safety | Protection | Anti-Islanding |  | Boolean | 4 | YES
P116 | Protection & Safety | Protection | SPD |  | Boolean | 3 | NO
P117 | Protection & Safety | Protection | Emergency Stop |  | Boolean | 4 | YES
P118 | Protection & Safety | Protection | Fire System Interlock |  | Boolean | 3 | NO
P119 | Protection & Safety | Protection | BMS Interlock |  | Boolean | 3 | NO
P120 | Protection & Safety | Protection | EMS Interlock |  | Boolean | 2 | NO
P121 | Protection & Safety | Protection | HVAC Interlock |  | Boolean | 1 | NO
P122 | Protection & Safety | Protection | Arc Fault Detection |  | Boolean | 2 | NO
P123 | Protection & Safety | Protection | SPD Type |  | Text | 1 | NO
P124 | Communication & Control | Comms | CAN |  | Boolean | 3 | NO
P125 | Communication & Control | Comms | Modbus TCP |  | Boolean | 4 | NO
P126 | Communication & Control | Comms | Modbus RTU |  | Boolean | 3 | NO
P127 | Communication & Control | Comms | IEC 61850 |  | Boolean | 4 | NO
P128 | Communication & Control | Comms | IEC 60870-5-104 |  | Boolean | 3 | NO
P129 | Communication & Control | Comms | Ethernet |  | Boolean | 3 | NO
P130 | Communication & Control | Comms | Fiber Optic |  | Boolean | 2 | NO
P131 | Communication & Control | Comms | SCADA Interface |  | Boolean | 4 | NO
P132 | Communication & Control | Comms | EMS Interface |  | Boolean | 4 | YES
P133 | Communication & Control | Comms | BMS Interface |  | Boolean | 5 | YES
P134 | Communication & Control | Comms | Remote Monitoring |  | Boolean | 3 | NO
P135 | Communication & Control | Comms | Remote Firmware Update |  | Boolean | 3 | NO
P136 | Communication & Control | Comms | NTP |  | Boolean | 1 | NO
P137 | Communication & Control | Comms | PTP |  | Boolean | 1 | NO
P138 | Communication & Control | Comms | GPS Time Synchronization |  | Boolean | 1 | NO
P139 | Communication & Control | Comms | Cybersecurity Features |  | Boolean | 3 | NO
P140 | Communication & Control | Comms | CAN Protocol |  | Text | 1 | NO
P141 | Mechanical | Dim | Length | mm | Lower_Better | 1 | NO
P142 | Mechanical | Dim | Width | mm | Lower_Better | 1 | NO
P143 | Mechanical | Dim | Height | mm | Lower_Better | 1 | NO
P144 | Mechanical | Dim | Weight | kg | Lower_Better | 2 | NO
P145 | Mechanical | Dim | Footprint | m² | Lower_Better | 3 | NO
P146 | Mechanical | Access | Mounting Method |  | Text | 1 | NO
P147 | Mechanical | Access | DC Cable Entry |  | Text | 1 | NO
P148 | Mechanical | Access | AC Cable Entry |  | Text | 1 | NO
P149 | Mechanical | Access | Top Cable Entry |  | Boolean | 1 | NO
P150 | Mechanical | Access | Bottom Cable Entry |  | Boolean | 1 | NO
P151 | Mechanical | Access | Front Access |  | Boolean | 2 | NO
P152 | Mechanical | Access | Rear Access |  | Boolean | 1 | NO
P153 | Mechanical | Access | Side Access |  | Boolean | 1 | NO
P154 | Mechanical | Access | Maintenance Clearance | mm | Lower_Better | 1 | NO
P155 | Mechanical | Calc | Footprint per MW | m²/MW | Lower_Better | 3 | NO
P156 | Mechanical | Calc | Weight per MW | kg/MW | Lower_Better | 2 | NO
P157 | Reliability & Lifecycle | Life | Design Life | years | Higher_Better | 3 | NO
P158 | Reliability & Lifecycle | Life | Expected Service Life | years | Higher_Better | 3 | NO
P159 | Reliability & Lifecycle | Life | MTBF | hours | Higher_Better | 3 | NO
P160 | Reliability & Lifecycle | Warranty | Warranty | years | Higher_Better | 4 | NO
P161 | Reliability & Lifecycle | Maint | Preventive Maintenance Interval | months | Higher_Better | 2 | NO
P162 | Reliability & Lifecycle | Maint | Fan Life | hours | Higher_Better | 1 | NO
P163 | Reliability & Lifecycle | Maint | Capacitor Life | hours | Higher_Better | 1 | NO
P164 | Reliability & Lifecycle | Maint | Cooling System Life | years | Higher_Better | 1 | NO
P165 | Reliability & Lifecycle | Maint | Filter Replacement Interval | months | Higher_Better | 1 | NO
P166 | Reliability & Lifecycle | Maint | Major Component Replacement | years | Higher_Better | 1 | NO
P167 | Reliability & Lifecycle | Service | Spare Parts Availability |  | Text | 3 | NO
P168 | Reliability & Lifecycle | Service | Local Service Support |  | Boolean | 4 | NO
P169 | Reliability & Lifecycle | Service | Local Service Engineer |  | Boolean | 3 | NO
P170 | Reliability & Lifecycle | Service | India Stock Availability |  | Boolean | 3 | NO
P171 | Certification & Compliance | Cert | IEC 62477-1 |  | Boolean | 5 | YES
P172 | Certification & Compliance | Cert | IEC 61000 Series |  | Boolean | 3 | NO
P173 | Certification & Compliance | Cert | IEC 62109 |  | Boolean | 3 | NO
P174 | Certification & Compliance | Cert | IEC 62933 |  | Boolean | 3 | NO
P175 | Certification & Compliance | Cert | UL 1741 |  | Boolean | 2 | NO
P176 | Certification & Compliance | Cert | UL 1741 SA |  | Boolean | 2 | NO
P177 | Certification & Compliance | Cert | UL 1741 SB |  | Boolean | 2 | NO
P178 | Certification & Compliance | Cert | UL 9540 |  | Boolean | 2 | NO
P179 | Certification & Compliance | Cert | IEEE 1547 |  | Boolean | 3 | NO
P180 | Certification & Compliance | Cert | IEEE 519 |  | Boolean | 3 | NO
P181 | Certification & Compliance | Cert | CE |  | Boolean | 3 | NO
P182 | Certification & Compliance | Cert | EMC |  | Boolean | 3 | NO
P183 | Certification & Compliance | Cert | Grid Code Compliance |  | Boolean | 5 | YES
P184 | Certification & Compliance | Cert | BIS |  | Boolean | 3 | NO
P185 | Certification & Compliance | Cert | Applicable Indian Standards |  | Text | 3 | NO
P186 | Certification & Compliance | Cert | Certificate Number |  | Text | 1 | NO
P187 | Certification & Compliance | Cert | Certificate Scope |  | Text | 1 | NO
P188 | Certification & Compliance | Cert | Certificate Expiry Date |  | Text | 1 | NO
P189 | BESS Integration | BESS | BMS Compatibility |  | Boolean | 5 | YES
P190 | BESS Integration | BESS | EMS Compatibility |  | Boolean | 5 | YES
P191 | BESS Integration | BESS | Battery Voltage Compatibility |  | Text | 4 | YES
P192 | BESS Integration | BESS | Battery Current Compatibility |  | Text | 3 | NO
P193 | BESS Integration | BESS | SOC Communication |  | Boolean | 3 | NO
P194 | BESS Integration | BESS | SOH Communication |  | Boolean | 2 | NO
P195 | BESS Integration | BESS | Charge Command |  | Boolean | 3 | NO
P196 | BESS Integration | BESS | Discharge Command |  | Boolean | 3 | NO
P197 | BESS Integration | BESS | Active Power Command |  | Boolean | 3 | NO
P198 | BESS Integration | BESS | Reactive Power Command |  | Boolean | 2 | NO
P199 | BESS Integration | BESS | Fast Power Response |  | Boolean | 3 | NO
P200 | BESS Integration | BESS | Pre-charge Sequence |  | Boolean | 2 | NO
P201 | BESS Integration | BESS | Contactor Control |  | Boolean | 2 | NO
P202 | BESS Integration | BESS | E-stop Integration |  | Boolean | 3 | NO
P203 | BESS Integration | BESS | Fire Alarm Integration |  | Boolean | 3 | NO
P204 | BESS Integration | BESS | HVAC Interlock |  | Boolean | 1 | NO
P205 | BESS Integration | BESS | Rack Communication |  | Boolean | 2 | NO
P206 | BESS Integration | BESS | DC Bus Compatibility |  | Boolean | 3 | NO
P207 | Commercial | Price | PCS Price | ₹ | Lower_Better | 3 | NO
P208 | Commercial | Price | Price Currency |  | Text | 1 | NO
P209 | Commercial | Price | Price per kW | ₹/kW | Lower_Better | 4 | NO
P210 | Commercial | Price | Price per MW | ₹/MW | Lower_Better | 3 | NO
P211 | Commercial | Cost | Installation Cost | ₹ | Lower_Better | 1 | NO
P212 | Commercial | Cost | Commissioning Cost | ₹ | Lower_Better | 1 | NO
P213 | Commercial | Cost | AMC Cost | ₹ | Lower_Better | 2 | NO
P214 | Commercial | Warranty | Warranty Years | years | Higher_Better | 2 | NO
P215 | Commercial | Cost | Extended Warranty Cost | ₹ | Lower_Better | 1 | NO
P216 | Commercial | Cost | Spare Parts Cost | ₹ | Lower_Better | 1 | NO
P217 | Commercial | Cost | Transportation Cost | ₹ | Lower_Better | 1 | NO
P218 | Commercial | Cost | Taxes/Duties | ₹ | Lower_Better | 1 | NO
P219 | Commercial | Cost | Total Delivered Cost | ₹ | Lower_Better | 3 | NO
P220 | Commercial | Calc | Total Cost per MW | ₹/MW | Lower_Better | 4 | NO

## Vendor_List
Vendor | Model | Type | Country | Contact | Notes
DemoVolt PCS-A | DV-2500-L | Central | — | — | DEMO
GridCore PCS-B | GC-2500-A | Central | — | — | DEMO
PowerStack PCS-C | PS-2200-L | String | — | — | DEMO — has critical failure

## Certification
Vendor | Standard | Certified(Y/N) | Certificate_Number | Edition | Scope | Rated_Power_Covered | Voltage_Covered | Cert_Date | Expiry_Date
DemoVolt PCS-A | IEC 62477-1
DemoVolt PCS-A | IEC 61000 Series
DemoVolt PCS-A | IEC 62109
DemoVolt PCS-A | IEC 62933
DemoVolt PCS-A | UL 1741
DemoVolt PCS-A | UL 1741 SA
GridCore PCS-B | IEC 62477-1
GridCore PCS-B | IEC 61000 Series
GridCore PCS-B | IEC 62109
GridCore PCS-B | IEC 62933
GridCore PCS-B | UL 1741
GridCore PCS-B | UL 1741 SA
PowerStack PCS-C | IEC 62477-1
PowerStack PCS-C | IEC 61000 Series
PowerStack PCS-C | IEC 62109
PowerStack PCS-C | IEC 62933
PowerStack PCS-C | UL 1741
PowerStack PCS-C | UL 1741 SA

## Commercial
Vendor | Model | PCS Price | Price Currency | Price per kW | Price per MW | Installation Cost | Commissioning Cost | AMC Cost | Warranty Years | Extended Warranty Cost | Spare Parts Cost | Transportation Cost | Taxes/Duties | Total Delivered Cost | Total Cost per MW
DemoVolt PCS-A | DV-2500-L
GridCore PCS-B | GC-2500-A
PowerStack PCS-C | PS-2200-L

## Scoring
SCORING METHOD
1. Parameter Score (0–10): Boolean PASS=10/FAIL=0; numeric PASS=8–10 by margin to Preferred; FAIL=3; N/A or Pending=excluded.
2. Category Score = weighted average of parameter scores in that category.
3. Weighted Score = Σ(Category Score/10 × Category Weight) / Σ(Weights) × 100.
4. Critical override: any Critical=YES parameter that FAILs → CRITICAL NON-COMPLIANCE; vendor cannot rank #1.
5. Live scores are computed in the HTML dashboard from the CSV; this sheet documents the method and category weights.
Category | Weight %
Basic Configuration | 4
DC Electrical | 7
AC Electrical | 8
Performance & Efficiency | 18
Overload Capability | 4
Grid Support | 14
Thermal & Environmental | 9
Protection & Safety | 9
Communication & Control | 5
Mechanical | 3
Reliability & Lifecycle | 5
Certification & Compliance | 7
BESS Integration | 4
Commercial | 3
TOTAL | 100

## Dashboard_Data
DASHBOARD_DATA
Export the PCS_Master_Data sheet as CSV (File → Save As → CSV UTF-8), name it PCS_Master_Data.csv, and upload it in the HTML dashboard.
The dashboard auto-detects vendors, computes compliance and scores, and refreshes all charts. No values are hard-coded in the HTML.